Stormwater Renewal Priority

Condition & Renewal Recommendation

Focus area: Auckland Local Board 175 (in-service stormwater network)

Prepared using: Auckland Council open data · PostGIS · Python (GeoPandas)

Analysis date: July 2026

# Summary

An asset-condition assessment of the in-service stormwater pipe network in Local Board 175 identified a small, well-defined set of pipes that should be prioritised for renewal. Of 20,086 in-service pipes assessed, 229 pipes — 1.1% of the network, approximately 5.6 km — score as high-priority for renewal. Targeting this 1.1% first offers a focused, affordable renewal programme rather than indiscriminate replacement.

# Renewal complexity: road-adjacency

A cross-layer spatial analysis (stormwater versus road centrelines, computed in PostGIS) found that 137 of the 229 high-priority pipes — roughly 60%, about 3 km — run within 10 metres of a road. These renewals carry added excavation, traffic-management and road-reinstatement cost, reinforcing the case for coordinated, early scheduling rather than reactive replacement after failure.

# Multi-asset spatial findings

Cross-referencing the priority pipes against roads and parks (spatial joins in PostGIS) surfaced two practical, cross-asset insights:

Road renewal coordination. 100 roads in the focus area sit within 10 m of high-priority pipe. The strongest candidates for coordinated road-and-pipe renewal — where digging once avoids repeat disruption — are Snells Beach Rd, Shelly Beach Rd, Baxter St (Warkworth), Creek Lane, and Percy St (Warkworth), each carrying significant lengths of aging pipe beneath or beside them.

Parks with buried priority assets. 19 parks contain high-priority stormwater pipe within their boundaries, meaning renewal there involves park land — access, reinstatement, and possible consent considerations. The most affected is a 12-hectare park holding 7 priority pipes (~394 m). Separately, 72 open-space parcels in the focus area are classed as stormwater-function land, linking green space directly to the drainage network.

# How priority was determined

Each pipe was scored 1–5 on three factors, then combined into a single weighted priority score (age 40%, material risk 35%, diameter/criticality 25%):

- Age — derived from installation date. Older pipes are closer to end of life.

- Material risk — brittle, legacy materials (earthenware, asbestos cement, brick) fail with less warning than modern PVC/PE.

- Diameter / criticality — larger-diameter mains carry greater consequence of failure.

Pipes scoring ≥ 3.5 were classed as high-priority.

# Key findings

- The high-priority group is more than twice the age of the network: 59.4 years average vs 28.6 years across the focus area.

- Legacy materials dominate the risk: 64 of the 229 high-priority pipes are asbestos cement (40) or earthenware (24) — the clearest renew-before-failure candidates.

- Large, aged concrete trunk mains (1960s, 900–2200 mm) combine advanced age with high criticality.

- Two concrete pipes installed in 1900 remain in service at 126 years — well beyond typical design life.

## High-priority pipe length by material

| Material | Pipes | Length (km) | Avg. priority |
| --- | --- | --- | --- |
| Concrete (CONC) | 164 | 3.97 | 3.62 |
| Asbestos cement (ABCM) | 40 | 1.12 | 3.77 |
| Earthenware (ERWR) | 24 | 0.55 | 3.66 |
| Concrete-lined (CCLS) | 1 | 0.01 | 3.90 |
| Total | 229 | 5.65 | — |

# Recommendation

- Prioritise the 64 asbestos-cement and earthenware pipes (~1.7 km combined) for near-term inspection and renewal — the highest failure-risk material in the network.

- Schedule condition inspection of the large-diameter 1960s concrete mains before committing to renewal, given the high consequence of failure.

- Flag the 1900-era pipes for immediate assessment as clear outliers beyond design life.

- Adopt the priority score as a repeatable screening tool, re-runnable across all Auckland local boards as data updates.

# Data quality notes

- Installation dates frequently record only the year (day/month are placeholders), so ages are reported to year resolution.

- A small number of records carry implausible or missing dates and were treated as medium priority rather than excluded.

- Analysis covers in-service pipes only (status = INSR); unverified records were excluded.

# Method & reproducibility

Data was filtered and cleaned in Python (GeoPandas), reprojected to NZ Transverse Mercator (EPSG:2193) for metric length calculations, scored, and loaded into a PostGIS spatial database. Summary length-by-material figures were computed in the database using spatial SQL (ST_Length). The full pipeline is reproducible from the accompanying notebook.

Built on an open-source stack (PostGIS · GeoPandas · Leaflet). The workflow is directly transferable to an Esri environment (ArcGIS Pro · Experience Builder · Survey123).